## User Notes
Condition Rating:
A | 1 | Good – Performing well and operating efficiently (the school buildings support the delivery of services to children and communities)
B | 0.75 | Satisfactory – Performing well but with minor problems (the school buildings generally support the delivery of services to children and communities)
C | 0.5 | Poor – Showing major problems and/or not operating optimally (the school buildings impede the delivery of activities that are needed for children and communities in the school)
D | 0.25 | Bad – Does not support the delivery of services to children and communities (the school buildings seriously impede the delivery of activities that are needed for children and communities in the school)
N/A |  | This covers elements that are not appicable, a score is attributed based on the average score of the applicable intermediate elements, within the the major element, thus ensuring no bias in scores. Note: If a n/a is selected the formula in on the Calc1 sheet in Column G (Adjusted Score) should be deleted and replaced with the appropriate elemental average score shown on at the bottom of column F (score) for each element.
Priority Ratings: | (Priority Ratings only Applicable to Short Term Works 1-5 year)
1 |  | Works required in year 1 that will prevent immediate closure of premises and/or address an immediate high risk to the health and safety of the occupants and/or remedy a serious breach of legislation.
2 |  | Work required in year 2 that will prevent serious deterioration of the fabric or services and/or address a medium risk to the health and safety of the occupants and/or remedy a minor breach of the legislation.
3 |  | Work required within 3 to 5 years that will prevent deterioration of the fabric or services and/or address a low risk to the health and safety of the occupants and/or a minor breach of the legislation.
Weightings
Major Element | Intermediate Element | Weighting (%)
Roof | Structure | 4
Roof | Covering | 4
Roof | Insulation | 1
Roof | Drainage | 1
Roof | Parapet, Handrails etc. | 1
Roof | Frame | 2
Roof | Other (Incl Chimneys) | 2
Roof Overall |  | 15
Floors & Stairs | Floor structure | 1.5
Floors & Stairs | Screed | 0.5
Floors & Stairs | Floor finishes | 1
Floors & Stairs | Staircases | 1.25
Floors & Stairs | Signage | 0.25
Floors & Stairs | Other | 0.5
Floors and Stairs Overall |  | 5
Ceilings (Ground & Upper Floors) |  | 2
Ceilings Overall |  | 2
External Walls, Windows & Doors | External Walls | 7.5
External Walls, Windows & Doors | External Doors | 3.25
External Walls, Windows & Doors | Windows | 5
External Walls, Windows & Doors | External Stairs, Steps & Access Ramps | 2
External Walls, Windows & Doors | Secondary Structures | 2
External Walls, Windows & Doors | Signage | 0.25
External Walls, Windows and Doors Overall |  | 20
Internal Walls & Doors | Internal Walls | 0.75
Internal Walls & Doors | Internal Linings / Finishes on Internal Walls | 0.5
Internal Walls & Doors | Internal Doors & Glazed Screens | 0.5
Internal Walls & Doors | Signage | 0.25
Internal Walls and Doors Overall |  | 2
Sanitary Services | Toilets | 2
Sanitary Services | Kitchens | 1
Sanitary Services Overall |  | 3
Mechanical Services | Heat Source & Equipment (e.g. Boilers incl. Flues) | 5
Mechanical Services | Heating | 4
Mechanical Services | Hot water | 2
Mechanical Services | Cold water | 2
Mechanical Services | Gas Storage & Distribution | 1
Mechanical Services | Oil Storage & Distribution* | 1
Mechanical Services | Ventilation | 1
Mechanical Services | Specialised Ventilation Systems | 0.5
Mechanical Services | Air Conditioning | 0.5
Mechanical Services | Fixed Fire Fighting Systems | 1.5
Mechanical Services | Plant/Equipment Supports or Foundations | 0.5
Mechanical Services Overall |  | 19
Electrical Services | Electrical Power | 5
Electrical Services | Lighting | 4
Electrical Services | Fire Precaution | 2
Electrical Services | Intruder Alarms | 1
Electrical Services | Lightning Protection | 0.25
Electrical Services | Communication Systems | 0.25
Electrical Services | Security Systems | 0.25
Electrical Services | Building Control Systems | 0.25
Electrical Services | Lifts & Hoists | 1
Electrical Services Overall |  | 14
Redecorations |  | 9
Redecoration Overall |  | 9
Fixed Internal Facilities, Furniture & Fittings | Teaching | 1.25
Fixed Internal Facilities, Furniture & Fittings | Non-teaching | 0.75
Fixed Internal Facilities, Furniture & Fittings Overall |  | 2
External Areas | Roads and Car Parks | 2
External Areas | Paths & Paved Pedestrian Areas | 2
External Areas | Walls, Fences & Gates | 1.25
External Areas | Signage | 0.25
External Areas | External Works / Infrastructure | 1.5
External Areas | Landscaping & Planting (Safety & Security) | 1
External Areas Overall |  | 8
Outdoor Sports Facilities and Permanent Fixed Furniture |  | 1
Fixed Internal Facilities, Furniture & Fittings Overall |  | 1
Total |  | 100

## Facility
Clackmannanshire Council - Condition Survey
Building Name: Dumyat Leisure Centre |  | Previous Rating: |  | Current Rating: B
Building Use: Leisure |  | Percentage Score: |  | Percentage Score: 77.5
Address: Main Street East, Menstrie |  | Date: 10/11/16 |  | Date:
UPRN: 35014257 |  |  |  | GIA | 1418
|  |  | Proposed Works | Priority Rating | Budget (£) | Projected Expenditure (by Year) | [29 empty] | Anticipated Maintenance items. | Maintenance contingency over element life
Major Element | Intermediate Elements | Condition |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | (£)
Roof | Structure | B |  |  | 0
Roof | Coverings (incl. Glazed Roof Lights) | B |  |  | 0 | [30 empty] | Slipped/damaged slate/tile etc. | 2187.6904
Roof | Insulation | B |  |  | 0
Roof | Drainage (incl. Rainwater Goods & Pipes) | B |  |  | 0 | [30 empty] | Replacement damaged/split sections of pipework and rainwater goods | 1904.0904
Roof | Parapets, Handrails etc. | N/A |  |  | 0
Roof | Frame | B |  |  | 0
Roof | Other (incl. Chimneys) | B | Paint soffit and facias, year 6 (See decorations for costs) | 3 | 0 | [30 empty] | Flaunching, leadwork, pointing etc. (N/A | 0
Floors & Stairs | Floor Structure (All Floors) | A |  |  | 0
Floors & Stairs | Screed (All Floors) | A |  |  | 0
Floors & Stairs | Floor Finishes (All Floors) | B | Replace carpet year 4, replace vinyl year 10, sand seal timber floor year 5 | 3 | 29520 | Projected Expenditure (by Year) 4: 9230; Projected Expenditure (by Year) 5: 2930; Projected Expenditure (by Year) 10: 5200; Projected Expenditure (by Year) 24: 9230; Projected Expenditure (by Year) 25: 2930
Floors & Stairs | Staircases | N/A |  |  | 0
Floors & Stairs | Signage | N/A |  |  | 0
Floors & Stairs | Other | N/A |  |  | 0
Ceilings (Ground & Upper Floors) | Ceilings | B |  |  | 0
External Walls, Windows & Doors | External Walls | B |  |  | 0 | [30 empty] | Pointing/spall repair of brickwork and stone. | 1386.095
External Walls, Windows & Doors | External Doors | B | Paint timber doors year 6 (See decorations for costs) |  | 0
External Walls, Windows & Doors | Windows | B | Replace rotten timber cills and glazing beads to windows, replace windows year 30 | 2 | 26490 | Projected Expenditure (by Year) 2: 10650; Projected Expenditure (by Year) 30: 15840
External Walls, Windows & Doors | External Stairs, Steps & Access Ramps | B |  |  | 0 | [30 empty] | Ramps and access handrails | 709
External Walls, Windows & Doors | Other Secondary Structures | N/A |  |  | 0
External Walls, Windows & Doors | Signage | B |  |  | 0
Internal Walls & Doors | Internal Walls | B |  |  | 0 | [30 empty] | Scuffs/collision damage of plasterwork and frame. | 1063.5
Internal Walls & Doors | Internal Linings / Finishes on Internal Walls | B |  |  | 0
Internal Walls & Doors | Internal Doors & Glazed Screens | B |  |  | 0
Internal Walls & Doors | Signage | B |  |  | 0
Sanitary Services | Toilets | A | Replace sanitaryware yr 14 |  | 6167 | Projected Expenditure (by Year) 14: 6167
Sanitary Services | Kitchens | A | Stainless fittings |  | 0
Mechanical Services | Heat Source & Equipment (e.g. Boilers incl. Flues) | B | Replace Hamworthy boilers yr 4 & 29 Replace Powermatic air heater yr 4 & 29 Replace Worcester boiler yr 20 Replave vertical calorifier yr 9 | 3 | 40400 | Projected Expenditure (by Year) 4: 17000; Projected Expenditure (by Year) 9: 4300; Projected Expenditure (by Year) 20: 2100; Projected Expenditure (by Year) 29: 17000
Mechanical Services | Heating | A | Replace LTHW system yr 9 |  | 19000 | Projected Expenditure (by Year) 9: 19000
Mechanical Services | Hot Water | A | Replace distribution yr 14 |  | 3200 | Projected Expenditure (by Year) 14: 3200
Mechanical Services | Cold Water | A | Replace distribution yr 14 |  | 3200 | Projected Expenditure (by Year) 14: 3200
Mechanical Services | Gas Storage & Distribution | A |  |  | 0
Mechanical Services | Oil Storage & Distribution | N/A |  |  | 0
Mechanical Services | Ventilation | B | Replace gym axial extract fan and local extracts yr 4 | 3 | 1900 | Projected Expenditure (by Year) 4: 1900
Mechanical Services | Specialised Ventilation Systems | A | Hall supply and extract system |  | 0
Mechanical Services | Air-Conditioning Plant, Systems & Controls | N/A |  |  | 0
Mechanical Services | Fixed Fire Fighting Systems | N/A |  |  | 0
Mechanical Services | Plant/Equipment Supports or Foundations | A |  |  | 0
Electrical Services | Electrical Power | B | Rewire lighting and power circuits to gym/store area yr 4 & 29. Replace remaining yr 20 | 3 | 142479 | Projected Expenditure (by Year) 4: 58647; Projected Expenditure (by Year) 20: 25185; Projected Expenditure (by Year) 29: 58647
Electrical Services | Lighting | B | Replace luminaires to gym /stores area yr 4 & 29. Replace remaining yr 20 | 3 | 55670 | Projected Expenditure (by Year) 4: 22915; Projected Expenditure (by Year) 20: 9840; Projected Expenditure (by Year) 29: 22915
Electrical Services | Fire Precaution | B | Replace fire alarm system yr 4 & 29 | 3 | 41092 | Projected Expenditure (by Year) 4: 20546; Projected Expenditure (by Year) 29: 20546
Electrical Services | Intruder Alarms | A | Replace system yr 15 |  | 4480 | Projected Expenditure (by Year) 15: 4480
Electrical Services | Lightning Protection | N/A |  |  | 0
Electrical Services | Communication Systems | A |  |  | 0
Electrical Services | Security Systems | A | Replace CCTV system yr 15 |  | 1800 | Projected Expenditure (by Year) 15: 1800
Electrical Services | Building Control Systems | B | Replace boiler control panel yr 4 | 3 | 6956 | Projected Expenditure (by Year) 4: 3478; Projected Expenditure (by Year) 24: 3478
Electrical Services | Lifts & Hoists | N/A |  |  | 0
Redecorations | Redecorations | B | Decorate toilet area year 1 and remaining year 6, paint handrails year 6, paint soffit and facias year 6 | 2 | 67640 | Projected Expenditure (by Year) 2: 910; Projected Expenditure (by Year) 6: 16000; Projected Expenditure (by Year) 13: 16910; Projected Expenditure (by Year) 20: 16910; Projected Expenditure (by Year) 27: 16910
Fixed Internal Facilities, Furniture & Fittings | Teaching | N/A |  |  | 0
Fixed Internal Facilities, Furniture & Fittings | Non-Teaching | B | Replace base units year 15 |  | 3490 | Projected Expenditure (by Year) 15: 3490
External Areas | Roads & Car Parks | B | Recover worn wearing surface to car park | 2 | 8060 | Projected Expenditure (by Year) 2: 4030; Projected Expenditure (by Year) 22: 4030 | line marking, minor repairs. | 3086.986
External Areas | Paths & Paved Pedestrian Areas | B | Recover sand carpet path year 20 |  | 350 | Projected Expenditure (by Year) 20: 350 | Minor defects, split flags/uneven edge kerbs etc. | 1234.7944
External Areas | Walls, Fences & Gates | B | Paint handrails year 6 |  | 0 | [30 empty] | Pointing/spall repair of external walls. | 1386.095
External Areas | Signage | B |  |  | 0
External Areas | External Works / Infrastructure | B |  |  | 0
External Areas | Landscaping & Planting (Safety & Security) | B |  |  | 0
Outdoor Sports Facilities and Permanent Fixed Furniture | Outdoor Sports Facilities and Permanent Fixed Furniture | B |  |  | 0
|  |  |  | TOTALS | 461894 | 0 | 15590 | 0 | 133716 | 2930 | 16000 | 0 | 0 | 23300 | 5200 | 0 | 0 | 16910 | 12567 | 9770 | 0 | 0 | 0 | 0 | 54385 | 0 | 4030 | 0 | 12708 | 2930 | 0 | 16910 | 0 | 119108 | 15840

## Calc1
Major Element | Intermediate Element | Weighting | Percentage (%) | Cond. | Score | Adjusted Score | Weighted Score | % | Rating
Roof | Structure | 4 | 26.6667 | B | 0.75 | 0.75 | 3 | 75 | B
Roof | Covering | 4 | 26.6667 | B | 0.75 | 0.75 | 3 | 75 | B
Roof | Insulation | 1 | 6.6667 | B | 0.75 | 0.75 | 0.75 | 75 | B
Roof | Drainage | 1 | 6.6667 | B | 0.75 | 0.75 | 0.75 | 75 | B
Roof | Parapet, Handrails etc. | 1 | 6.6667 | N/A | 0 | 0 | 0 | 0
Roof | Frame | 2 | 13.3333 | B | 0.75 | 0.75 | 1.5 | 75 | B
Roof | Other (Incl Chimneys) | 2 | 13.3333 | B | 0.75 | 0.75 | 1.5 | 75 | B
Roof Overall |  | 15 | 100 |  | 0.75 |  | 10.5 | 70 | B
Floors & Stairs | Floor structure | 1.75 | 35 | A | 1 | 1 | 1.75 | 100 | A
Floors & Stairs | Screed | 0.5 | 10 | A | 1 | 1 | 0.5 | 100 | A
Floors & Stairs | Floor finishes | 1.25 | 25 | B | 0.75 | 0.75 | 0.9375 | 75 | B
Floors & Stairs | Staircases | 1.25 | 25 | N/A | 0 | 0.92 | 1.15 | 92 | A
Floors & Stairs | Signage | 0.25 | 5 | N/A | 0 | 0.92 | 0.23 | 92 | A
Floors & Stairs | Other | 0 | 0 | N/A | 0 | 0 | 0 | 0 | N/A
Floors and Stairs Overall |  | 5 | 100 |  | 0.91667 |  | 4.5675 | 91.35 | A
Ceilings (Ground & Upper Floors) |  | 2 | 100 | B | 0.75 | 0.75 | 1.5 | 75 | B
Ceilings Overall |  | 2 | 100 |  | 0.75 |  |  | 75 | B
External Walls, Windows & Doors | External Walls | 7.5 | 37.5 | B | 0.75 | 0.75 | 5.625 | 75 | B
External Walls, Windows & Doors | External Doors | 3.25 | 16.25 | B | 0.75 | 0.75 | 2.4375 | 75 | B
External Walls, Windows & Doors | Windows | 5 | 25 | B | 0.75 | 0.75 | 3.75 | 75 | B
External Walls, Windows & Doors | External Stairs, Steps & Access Ramps | 2 | 10 | B | 0.75 | 0.75 | 1.5 | 75 | B
External Walls, Windows & Doors | Secondary Structures | 2 | 10 | N/A | 0 | 0 | 0 | 0
External Walls, Windows & Doors | Signage | 0.25 | 1.25 | B | 0.75 | 0.75 | 0.1875 | 75 | B
External Walls, Windows and Doors Overall |  | 20 | 100 |  | 0.75 |  |  | 67.5 | B
Internal Walls & Doors | Internal Walls | 0.75 | 37.5 | B | 0.75 | 0.75 | 0.5625 | 75 | B
Internal Walls & Doors | Internal Linings / Finishes on Internal Walls | 0.5 | 25 | B | 0.75 | 0.75 | 0.375 | 75 | B
Internal Walls & Doors | Internal Doors & Glazed Screens | 0.5 | 25 | B | 0.75 | 0.75 | 0.375 | 75 | B
Internal Walls & Doors | Signage | 0.25 | 12.5 | B | 0.75 | 0.75 | 0.1875 | 75 | B
Internal Walls and Doors Overall |  | 2 | 100 |  | 0.75 |  |  | 75 | B
Sanitary Services | Toilets | 2 | 66.6667 | A | 1 | 1 | 2 | 100 | A
Sanitary Services | Kitchens | 1 | 33.3333 | A | 1 | 1 | 1 | 100 | A
Sanitary Services Overall |  | 3 | 100 |  | 1 |  |  | 100 | A
Mechanical Services | Heat Source & Equipment (e.g. Boilers incl. Flues) | 5 | 26.3158 | B | 0.75 | 0.75 | 3.75 | 75 | B
Mechanical Services | Heating | 4 | 21.0526 | A | 1 | 1 | 4 | 100 | A
Mechanical Services | Hot water | 2 | 10.5263 | A | 1 | 1 | 2 | 100 | A
Mechanical Services | Cold water | 2 | 10.5263 | A | 1 | 1 | 2 | 100 | A
Mechanical Services | Gas Storage & Distribution | 2 | 10.5263 | A | 1 | 1 | 2 | 100 | A
Mechanical Services | Oil Storage & Distribution | 0 | 0 | N/A | 0 | 0 | 0 | 0 | N/A
Mechanical Services | Ventilation | 1 | 5.2632 | B | 0.75 | 0.75 | 0.75 | 75 | B
Mechanical Services | Specialised Ventilation Systems | 0.5 | 2.6316 | A | 1 | 1 | 0.5 | 100 | A
Mechanical Services | Air Conditioning | 0.5 | 2.6316 | N/A | 0 | 0 | 0 | 0
Mechanical Services | Fixed Fire Fighting Systems | 1.5 | 7.8947 | N/A | 0 | 0 | 0 | 0
Mechanical Services | Plant/Equipment Supports or Foundations | 0.5 | 2.6316 | A | 1 | 1 | 0.5 | 100 | A
Mechanical Services Overall |  | 19 | 100 |  | 0.9375 |  |  | 81.5789 | B
Electrical Services | Electrical Power | 5 | 35.7143 | B | 0.75 | 0.75 | 3.75 | 75 | B
Electrical Services | Lighting | 4 | 28.5714 | B | 0.75 | 0.75 | 3 | 75 | B
Electrical Services | Fire Precaution | 2 | 14.2857 | B | 0.75 | 0.75 | 1.5 | 75 | B
Electrical Services | Intruder Alarms | 1 | 7.1429 | A | 1 | 1 | 1 | 100 | A
Electrical Services | Lightning Protection | 0.25 | 1.7857 | N/A | 0 | 0 | 0 | 0
Electrical Services | Communication Systems | 0.25 | 1.7857 | A | 1 | 1 | 0.25 | 100 | A
Electrical Services | Security Systems | 0.25 | 1.7857 | A | 1 | 1 | 0.25 | 100 | A
Electrical Services | Building Control Systems | 0.25 | 1.7857 | B | 0.75 | 0.75 | 0.1875 | 75 | B
Electrical Services | Lifts & Hoists | 1 | 7.1429 | N/A | 0 | 0 | 0 | 0
Electrical Services Overall |  | 14 | 100 |  | 0.85714 |  |  | 70.9821 | B
Redecorations |  | 9 | 100 | B | 0.75 | 0.75 | 6.75 | 75 | B
Redecoration Overall |  | 9 | 100 |  | 0.75 |  |  | 75 | B
Fixed Internal Facilities, Furniture & Fittings | Teaching | 1.25 | 62.5 | N/A | 0 | 1 | 1.25 | 100 | A
Fixed Internal Facilities, Furniture & Fittings | Non-teaching | 0.75 | 37.5 | B | 0.75 | 0.75 | 0.5625 | 75 | B
Fixed Internal Facilities, Furniture & Fittings Overall |  | 2 | 100 |  | 0.75 |  |  | 90.625 | A
External Areas | Roads and Car Parks | 2 | 25 | B | 0.75 | 0.75 | 1.5 | 75 | B | 0 | C | 0.5
External Areas | Paths & Paved Pedestrian Areas | 2 | 25 | B | 0.75 | 0.75 | 1.5 | 75 | B
External Areas | Walls, Fences & Gates | 1.25 | 15.625 | B | 0.75 | 0.75 | 0.9375 | 75 | B
External Areas | Signage | 0.25 | 3.125 | B | 0.75 | 0.75 | 0.1875 | 75 | B
External Areas | External Works / Infrastructure | 1.5 | 18.75 | B | 0.75 | 0.75 | 1.125 | 75 | B
External Areas | Landscaping & Planting (Safety & Security) | 1 | 12.5 | B | 0.75 | 0.75 | 0.75 | 75 | B
External Areas Overall |  | 8 | 100 |  | 0.75 |  |  | 75 | B
Outdoor Sports Facilities and Permanent Fixed Furniture |  | 1 | 100 | B | 0.75 | 0.75 | 0.75 | 75 | B
Outdoor Sports Facilities and Permanent Fixed Furniture Overall |  | 1 | 100 |  | 0.75 |  |  | 75 | B

## Calc2
Element | Condition Rating | Condition | Score | Element Weighting (%) | Weighted Score
Roofs | B | SAT | 0.75 | 15 | 11.25
Floors & Stairs | A | GOOD | 1 | 5 | 5
Ceilings | B | SAT | 0.75 | 2 | 1.5
External Walls etc. | B | SAT | 0.75 | 20 | 15
Internal Walls etc. | B | SAT | 0.75 | 2 | 1.5
Sanitary Services | A | GOOD | 1 | 3 | 3
Mechanical Services | B | SAT | 0.75 | 19 | 14.25
Electrical Services | B | SAT | 0.75 | 14 | 10.5
Redecoration | B | SAT | 0.75 | 9 | 6.75
Fixed Internal Facilities | A | GOOD | 1 | 2 | 2
External Areas | B | SAT | 0.75 | 8 | 6
Outdoor Sports Facilities and Permanent Fixed Furniture | B | SAT | 0.75 | 1 | 0.75
Total |  |  |  | 100 | 77.5
Overall Property Condition |  |  |  | 77.5 | B
SAT

## Statutory
Clackmannanshire Council - Statutory Documentation/Risk assessments
Building Name: Dumyat Leisure Centre |  | Previous Rating: |  | UPRN: 35014257
Building Use: Leisure |  | Current Rating:
Address: Main Street East, Menstrie |  | Date: 10/11/16
|  | Rank A-D | Proposed Works | Priority Rating | Budget (£)
Main Element | Sub-element
COMPLIANCE WITH FIRECODE | RISK ASSESSMENTS | A | Fire risk assessment dated August 2012 in need of review | 2 | 500
ASBESTOS | ASBESTOS REGISTER | A | Survey carried out 28/04/02
CONTROL OF LEGIONELLA | RISK ASSESSMENTS | A | Risk assessment carried out 05/06/15 by Cleartech
HEALTH & SAFETY AT WORK ACT 1974 | SAFETY GLAZING | B | No obvious internal/ external safety glazing noted. Include in general health and Safety risk assessment.
COSHH REGULATIONS | STORAGE, VENTILATION AND WARNING SIGNAGE | A | COSHH Data sheets provided
PRESSURE SYSTEMS | WRITTEN SCHEME OF EXAMINATION | N/A | Check pressure/volume rating of Boss expansion vessel
MAINTENANCE & OPERATION OF EQUIPMENT IN CONFINED SPACES | ACCESS AND VENTILATION | N/A
STORAGE OF FLAMMABLE SUBSTANCES | LIQUIDS, GASES AND OTHER MATERIALS | N/A | No flammable gases/liquids noted.
ELECTRICAL SERVICES - SUPPLY & DISTRIBUTION | FIXED ELECTRICAL INSTALLATION TESTING | B | Fixed installation notice on distribution boards indicate tests carried out 2015. No test certificated provided
HEALTH & SAFETY AT WORK ACT 1974 | ADEQUATE PROVISION OF LIGHTING | A
MISCELLANEOUS | MISCELLANEOUS | N/A
|  |  |  | TOTALS | 500

## Function
Clackmannanshire Council - Functional Suitability
Building Name: Dumyat Leisure Centre |  |  | Previous Rating: |  | UPRN: 35014257
Building Use: Leisure |  |  | Current Rating:
Address: Main Street East, Menstrie |  |  | Date: 10/11/16
Main Element | Component | Rank A - D | Score 1 - 10 | Problems / Deficiencies | Opportunities | Budget
INTERNAL SPACE RELATIONSHIPS | CRITICAL DIMENSIONS ARE SUITABLE FOR THE FUNCTION | A | 10 | No issues noted. No specific published guidance is available regarding to dimensions for this type of property |  | 0
INTERNAL SPACE RELATIONSHIPS | HOW WELL IS THE BUILDING FUNCTIONING | B | 8 | Staff reported the building functioned well, apart from the library area needs partitioning off from the remainder of the building, when school sports sessions are held in the gym, as children get distracted and try to use the library. | Provide scissor door partitions. | 4000
INTERNAL SPACE RELATIONSHIPS | HOW FLEXIBLE IS THE BUILDING IN TERMS OF USING IT FOR DIFFERENT TYPES OF BUILDING SPACE | A | 10 | The property was built with multi function use in mind, currently used as a gym/library/community meeting/function. |  | 0
INTERNAL SPACE RELATIONSHIPS | IS THE LAYOUT AND ARRANGEMENT OF THE BUILDING SUITABLE FOR THE BUILDING USERS WITH APPROPRIATE AND ADEQUATE AMENITIES PROVIDED | A | 10 | Apart from the partitions, staff reported the building well suited with good amenities. |  | 0
INTERNAL SPACE RELATIONSHIPS | SECURITY IS MAINTAINED | A | 10 | Intruder alarm installed. |  | 0
SUPPORT FACILITIES | ADEQUATE TOILETS FOR THE NUMBER OF USERS | A | 10 | No guidance for this type of property. |  | 0
SUPPORT FACILITIES | ADEQUATE STORAGE SPACE | A | 10 | Large storage areas to rear of property. |  | 0
SUPPORT FACILITIES | PROVISION HAS BEEN MADE FOR DISABLED PEOPLE | n |  | See separate DDA report. |  | 0
LOCATION | RELATIONSHIP TO CAR PARKING AREAS IS CLEAR AND REASONABLY CLOSE | A | 10 | Integral public car park |  | 0
LOCATION | ACCESS TO PUBLIC TRANSPORT LINKS IS GOOD | A | 10 | Adjacent to local bus routes. |  | 0
LOCATION | ACCESS VIA VERTICAL OR HORIZONTAL COMMUNICATION (LIFTS, STAIRS) IS GOOD | A | 10 |  |  | 0
[5 empty] | Total Cost | 4000

## Space
Clackmannanshire Council - Space Utilisation
Building Name: Dumyat Leisure Centre |  |  | Previous Rating: |  | UPRN: 35014257
Building Use: Leisure |  |  | Current Rating: U
Address: Main Street East, Menstrie |  |  | Date: 10/11/16
Main Element | Component | Rank (O, F, U, E) | Problems / Deficiencies | Opportunities | Budget
CURRENT USE | HOW INTENSIVE IS USE OF SPACE | U | Mon and Wed open 9.00 - 21.00, Tue, Thur, Fri 1.00 - 21.00 Sat 9.30 - 12.00 with ad hoc opening if additional bookings are taken. Staff reported the premises can be under utilized at times dependant on community use. | Look into additional usage for the property, with additional sports usage by local primary schools. | 0
USE OVER TIME | DOES USAGE VARY OVER TIME (DAILY, WEEKLY) | U | Usage dependant on community bookings. |  | 0
GUIDANCE | DOES AVAILABLE SPACE COMPLY WITH NATIONAL GUIDANCE | n | There is no specific guidance for this type of property and considered suitable for its current use |  | 0
|  |  |  | Total Cost | 0

## Quality
Clackmannanshire Council - Quality
Building Name: Dumyat Leisure Centre |  |  | Previous Rating: |  | UPRN: 35014257
Building Use: Leisure |  |  | Current Rating: A
Address: Main Street East, Menstrie |  |  | Date: 10/11/16
Main Element | Component | Rank A - D | Score 1 - 10 | Problems / Deficiencies | Opportunities | Budget
AMENITY | ATTRACTIVE MAIN ENTRANCE/ RECEPTION AREA/ DEPARTMENTS | A | 10 | Pleasant modern reception. |  | 0
AMENITY | TOILET FACILITIES ARE WELL PROVIDED | A | 10 |  |  | 0
AMENITY | APPROPRIATE STORAGE PROVISION HAS BEEN MADE | A | 10 | Large storage areas to rear of property. |  | 0
AMENITY | DISABLED USERS ARE CATERED FOR | n |  | See separate DDA report. |  | 0
AMENITY | SEATING AND WAITING AREAS ARE SUFFICIENT | A | 10 | Multiple seating areas surrounding property. |  | 0
AMENITY | APPROPRIATE SAFETY AND SECURITY MEASURES ARE IN PLACE | A | 10 | Intruder alarm installed. |  | 0
AMENITY | ADEQUATE CAR PARKING FACILITIES | A | 10 | Integral public car park |  | 0
AMENITY | ACCESSIBLE BY PUBLIC AND PRIVATE TRANSPORT | A | 10 | Adjacent to local bus routes. |  | 0
COMFORT ENGINEERING | ARTIFICIAL LIGHTING ENHANCES OVERALL DESIGN | A | 10 |  |  | 0
COMFORT ENGINEERING | COMFORT CONDITIONS ARE ACHIEVED IN HEATING | A | 10 | Staff reported the heating controls are poor being cold in the winter and too hot in the summer months. | Investigate heating controls and amend to suit the properties needs. | 0
COMFORT ENGINEERING | COMFORT CONDITIONS ARE ACHIEVED IN VENTILATION | A | 10 | Staff reported no issues with the ventilation system. |  | 0
COMFORT ENGINEERING | PERSISTENT ODOURS ARE ABSENT | A | 10 |  |  | 0
DESIGN | LANDSCAPING IS ATTRACTIVE | A | 10 |  |  | 0
DESIGN | NATURAL DAYLIGHT IS USED TO OPTIMUM EFFECT | A | 10 |  |  | 0
DESIGN | APPROPRIATE FINISHES ARE USED TO FLOORS, CEILINGS AND WALLS | A | 10 |  |  | 0
DESIGN | FURNITURE COORDINATES WELL WITH OVERALL DESIGN | A | 10 |  |  | 0
DESIGN | GOOD MAINTENANCE AND CLEANLINESS | A | 10 | Clean and tidy throughout. |  | 0
[5 empty] | Total Cost | 0

## Environment
Clackmannanshire Council - Environmental Management
Building Name: Dumyat Leisure Centre |  |  | Previous Rating: |  |  | UPRN: 35014257
Building Use: Leisure |  |  | Current Rating: G
Address: Main Street East, Menstrie |  |  | Date: 10/11/16
ENERGY PERFORMANCE | Energy Consumption kWh/m2/yr | EPC rating | Potential EPC rating | EPC Benchmark for new build | CIBSE Energy benchmark | EPC certificate Improvements | Actual/Benchmark comparison
ENERGY PERFORMANCE | 147.7 | G | G | D | 270 | Install more efficient hot water heater/Replace fluorescent lighting/Add optimum start heating control/Install cavity wall insulation. Energy consumption compares favourably with published benchmarks. | 0.54704
Total

## DDA
Clackmannanshire Council - Functional Suitability
Building Name: Dumyat Leisure Centre |  |  | Previous Rating: |  | UPRN: 35014257
Building Use: Leisure |  |  | Current Rating:
Address: Main Street East, Menstrie |  |  | Date: 10/11/16
Main Element | Component | Rank A - D | Score 1 - 10 | Priority (Low/ Low-Medium/ Medium-High/High) | Problems / Deficiencies | Opportunities | Budget
EXTERNAL APPROACH | APPROACH ROUTES AND STREET FURNITURE | A | 10 |  |  |  | 0
EXTERNAL APPROACH | CAR PARKING | B | 8 | Low | Single parking space provided with poor markings and no posted signage to indicate position within the car park | Re mark out the disabled parking space and provide posted signage to indicate position | 730
EXTERNAL APPROACH | EXTERNAL STEPS | n |  |  |  |  | 0
EXTERNAL APPROACH | EXTERNAL RAMPS | n |  |  |  |  | 0
ENTRANCE-RECEPTION | MAIN ENTRANCE- SIGNAGE | A | 10 |  |  |  | 0
ENTRANCE-RECEPTION | ENTRANCE DOOR | A | 10 |  | Power assisted doors |  | 0
ENTRANCE-RECEPTION | INTERCOM SYSTEM | n |  |  |  |  | 0
ENTRANCE-RECEPTION | ENTRANCE LOBBY/FOYER | A | 10 |  |  |  | 0
ENTRANCE-RECEPTION | COUNTER/SERVICE DESKS | A | 10 |  |  |  | 0
ENTRANCE-RECEPTION | TELEPHONES | n |  |  |  |  | 0
CIRCULATION HORIZONTAL/ VERTICAL | CORRIDORS | A | 10 |  | No issues noted |  | 0
CIRCULATION HORIZONTAL/ VERTICAL | INTERNAL STAIRS | n |  |  |  |  | 0
CIRCULATION HORIZONTAL/ VERTICAL | INTERNAL RAMPS | n |  |  |  |  | 0
CIRCULATION HORIZONTAL/ VERTICAL | LIFTS | n |  |  |  |  | 0
CIRCULATION HORIZONTAL/ VERTICAL | INTERNAL DOORS | A | 10 |  | Vision panels to circulation doors |  | 0
INTERNAL SPACES | SEATING | A | 10 |  |  |  | 0
INTERNAL SPACES | SURGERIES/ TREATMENT ROOMS/ OFFICES | A | 10 |  | No access issues noted |  | 0
INTERNAL SPACES | COUNTERS AND SERVICE DESKS | A | 10 |  |  |  | 0
INTERNAL SPACES | ALARMS | C | 6 | High | No audio/visual alarm within disabled toilet | Fit alarms | 600
INTERNAL SPACES | WAYFINDING | A | 10 |  | No issues noted |  | 0
INTERNAL SPACES | LIGHTING | A | 10 |  |  |  | 0
INTERNAL SPACES | ACOUSTICS | A | 10 |  |  |  | 0
SANITARY FACILITIES | WC'S DISABLED | C | 6 | Medium | The disabled toilet facilities do not have single lever mixer taps or have an emergency pull chord alarm fitted | Replace existing with single lever mixer tap and install pull chord alarm | 700
SANITARY FACILITIES | OTHER SANITARY FACILITIES | A | 10 |  |  |  | 0
EVACUATION MANAGEMENT, IMPLEMENTATION | WAYFINDING | A | 10 |  | No issues noted |  | 0
EVACUATION MANAGEMENT, IMPLEMENTATION | MEANS OF ESCAPE | n |  |  | Good directional emergency lighting |  | 0
EVACUATION MANAGEMENT, IMPLEMENTATION | BUILDING MANAGEMENT | A | 10 |  |  |  | 0
[6 empty] | Total | 2030